## OVERALL ESTIMATE (hidden)
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidder must complete each tab for submission to be considered reponsive; sheet below will auto populate with totals.
LIFT STATION REHABILITATION
| ITEM NO. | DESCRIPTION |  | UNITS | QTY. | UNIT PRICE ($) | EXTENDED PRICE ($) | New 301 Ind Park | Lakewood Meadows | Mote Ranch 3 | 41A | Arnold Palmer Green 1
1AA | 1 | Wetwell Cleaning |  | SF | 3058 |  | 0 | 0 | 0 | 0 | 0 | 0
4-8AA | 2 | Wetwell Discharge Piping, HDPE DR-11 |  | LF | 253 |  | 0 | 0 | 0 | 0 | 0 | 0
20-22AA | 3 | Pump Base Ells, BPIU |  | EA | 11 |  | 0 | 0 | 0 | 0 | 0 | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 11 |  | 0 | 0 | 0 | 0 | 0 | 0
26-32AA | 5 | S.S. Pipe Bracing |  | EA | 15 |  | 0 | 0 | 0 | 0 | 0 | 0
34-37AA | 6 | Modify Existing Rim Elevation
| 6.1 | Wet Well |  | VF | 2.5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 7 | Replace Existing Top Slab
38-41AA | 7.1 | Wet Well |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
| 7.2 | Valve Vault |  | EA | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 8 | PVC Vent, Sch 80 |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
42-48AA | 9 | Aluminum Hatch Cover, varies, single door (Wetwell) |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
42-48AA | 10 | Aluminum Hatch Cover, 48" x 48", double door (Valve Vault) |  | EA | 1 |  | 0 | 0 | 0 | 0 | 0
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 227 |  | 0 | 0 | 0 | 0 | 0 | 0
54-58AA | 12 | Resilient (Link) Seals w/ Carrier Pipe & Liner Repair |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
59-65AA | 13 | Liner, spray-on |  | SF | 1776 |  | 0 | 0 | 0 | 0 | 0 | 0
| 14 | Repair Ex. Liner, if required |  | SF | 2192 |  | 0 | 0 | 0 | 0 | 0 | 0
71-72AA | 15 | Remove & Replace Ex. PVC Drain P-trap (regrout) & Liner Repair |  | EA | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 16 | Grout Fill Ex. Drain, abandon |  | EA | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
73-77AA | 17 | Gate Valve, FLG |  | EA | 12 |  | 0 | 0 | 0 | 0 | 0 | 0
78-82AA | 18 | Swing Check Valve, FLG |  | EA | 8 |  | 0 | 0 | 0 | 0 | 0 | 0
101-105AA | 19 | Gate Valve, MJ |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
83-87AA | 20 | Pipe, D.I., FLG |  | LF | 15 |  | 0 | 0 | 0 | 0 | 0 | 0
106-110AA | 21 | Pipe, PVC (DR-18) |  | LF | 55 |  | 0 | 0 | 0 | 0 | 0 | 0
88AA | 22 | Fittings, type varies | [5 empty] | 0 | 0 | 0 | 0 | 0
| 22.1 | Tee |  | EA | 6 |  | 0 | 0 | 0 | 0 | 0 | 0
| 22.2 | Cross |  | EA | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 22.3 | 90 |  | EA | 7 |  | 0 | 0 | 0 | 0 | 0 | 0
| 22.4 | 90 |  | EA | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
| 22.5 | 45 |  | EA | 6 |  | 0 | 0 | 0 | 0 | 0 | 0
90-94AA | 23 | Coupling Adapters, D.I., FLG |  | EA | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
95-96AA | 24 | Quick Coupler Adapter, aluminum, male, w/ alum dust |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
97AA | 25 | S.S. Adjustable Valve Supports, FLG attachment |  | EA | 10 |  | 0 | 0 | 0 | 0 | 0 | 0
| 26 | Abandon Existing Structure |  | LS | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
| 27 | Concrete Slab, Valve Assembly |  | LS | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
116-123AA | 28 | Influent Line Plug |  | EA | 6 |  | 0 | 0 | 0 | 0 | 0 | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
129AA | 30 | Water Service Connection and Line, 2" |  | LF | 100 |  | 0 | 0 | 0 | 0 | 0 | 0
| 31 | Upgrade / Relocate Ex. Meter, Backflow, & Hose Bibb Assembly |  | EA | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
| 32 | Replace Ex. Tapping Saddle; Install Brass Plug |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
1AB | 33 | Remove & Replace Electric Meter Can |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
2AB | 34 | Remove & Replace Fused Safety Switch (disconnect) |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
4AB | 35 | Remove & Replace Control Panel |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 37 | Junction Box, 304 SS |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 150 |  | 0 | 0 | 0 | 0 | 0 | 0
25AB | 39 | Remove & Replace Electrical Service |  | LF | 40 |  | 0 | 0 | 0 | 0 | 0 | 0
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
| 43 | Washed Shell with Weed Barrier |  | SY | 206 |  | 0 | 0 | 0 | 0 | 0 | 0
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 1711 |  | 0 | 0 | 0 | 0 | 0 | 0
19A | 45 | Install New Lift Station Driveway, 6" thick concrete |  | SY | 205 |  | 0 | 0 | 0 | 0 | 0 | 0
| 46 | Sodding |  | SY | 420 |  | 0 | 0 | 0 | 0 | 0 | 0
| 47 | New Conc. Floor & Fillet, 4,000 psi |  | CY | 10 |  | 0 | 0 | 0 | 0 | 0 | 0
| 48 | Tree/Brush Removal |  | EA | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
| 49 | Fill Dirt, clean and compacted |  | CY | 35 |  | 0 | 0 | 0 | 0 | 0 | 0
| 50 | Concrete Retaining Wall w/ Aluminum Safety Rail |  | LS | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 51 | Re-Install Ex. Meter Vault Top & Gate Valve Removal |  | LS | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 52 | Install Drop Bowl, gravity influent |  | EA | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
EMERGENCY GENERATOR REMOVAL-EMERGENCY BACKUP PUMP INSTALLATION - ARNOLD PALMER GREEN 1 ONLY
| 53 | Site Demolition |  | LS | 1 |  | 0 |  |  |  |  | 0
| 54 | Reinforced Concrete Slab (poured in place) |  | SY | 15 |  | 0 |  |  |  |  | 0
| 55 | Emergency Backup Pump & Fuel Tank |  | LS | 1 |  | 0 |  |  |  |  | 0
| 56 | PVC Pipe (C900, DR-18), 6" (Pump Discharge Line) |  | LF | 26 |  | 0 |  |  |  |  | 0
| 57 | HDPE DR-11, 8" (Pump Suction Line) |  | LF | 32 |  | 0 |  |  |  |  | 0
| 58 | Ductile Iron Fittings
| 58.1 | Red., FLG, 4"x6" (pump connection fitting, adjust as necessary) |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.2 | Red., FLG, 4"x8" (pump connection fitting, adjust as necessary) |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.3 | 45, MJ, 6" |  | EA | 2 |  | 0 |  |  |  |  | 0
| 58.4 | 90, FLG, 6" |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.5 | 45, FLG, 8" |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.6 | 90, FLG. 8" |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.7 | 90, MJ, 8" |  | EA | 1 |  | 0 |  |  |  |  | 0
| 58.8 | 90, HDPE Molded , Fusion Welded, 8" |  | EA | 1 |  | 0 |  |  |  |  | 0
| 59 | Sch 80 PVC Conduit, 2" |  | LF | 15 |  | 0 |  |  |  |  | 0
| 60 | Level Transducer, GXS3-PP300-A49-B49-50-C01-D49 |  | EA | 1 |  | 0 |  |  |  |  | 0
| 61 | PVC Stilling Well, 6" |  | LF | 28 |  | 0 |  |  |  |  | 0
| 62 | Permits |  | LS | 1 |  | 0 |  |  |  |  | 0
|  | Subtotal Construction Cost |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 63 | Mobilization |  | LS |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 64 | Record Drawings |  | LS |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Construction Cost |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
400-0-11; Concrete Class NS, Gravity Wall; CY
515-2311; Handrail, Aluminum, 42" Type 1; LF
| 1 | Tree Removal
| 1.01 | 4.1"-6" | EA | 7 |  | 0
| 1.02 | 6.1"-12" | EA | 6 |  | 0
| 1.03 | 12.1"-24" or Cluster Equivalent | EA | 1 |  | 0

## New 301 Ind Park 344
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidders must provide prices for each available line item on each tab for their bid to be considered responsive.
LIFT STATION REHABILITATION - NEW 301 INDUSTRIAL PARK RTU 344 (Project No. 5156090)
| ITEM NO. | DESCRIPTION |  | U/M | QTY. | UNIT PRICE | EXTENDED PRICE ($)
1AA | 1 | Wetwell Cleaning |  | SF | 84 |  | 0
4-8AA | 2 | Wetwell Discharge Piping, PVC (SCH 80) 2" |  | LF | 27 |  | 0 |  | 2
20-22AA | 3 | Pump Base Ells, BPIU-12 |  | EA | 2 |  | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 2 |  | 0
26-32AA | 5 | S.S. Pipe Bracing, 4 ft dia. |  | EA | 2 |  | 0
34-37AA | 6 | Modify Existing Rim Elevation
| 6.1 | Wet Well, lower |  | VF | 0.5 |  | 0
| 7 | Replace Existing Top Slab
38-41AA | 7.1 | Wet Well |  | EA | 1 |  | 0
| 7.2 | Valve Vault |  | EA | 1 |  | 0
| 8 | PVC Vent, Sch 80, 4" |  | EA | 1 |  | 0
42-48AA | 9 | Aluminum Hatch Cover, 30" x 42", single door (Wetwell) |  | EA | 1 |  | 0 |  |  |  |  | Hatch Cover Size Requirements
42-48AA | 10 | Aluminum Hatch Cover, 48" x 48", double door (Valve Vault) |  | EA | 1 |  | 0 |  |  |  |  | Disch Pipe Size |  | Hatch Size | WW Dia. Range
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 10 |  | 0 |  |  |  |  | 3" |  | 30"x32" | 41" | *side-out let tee
54-58AA | 12 | Resilient (Link) Seals w/ Carrier Pipe & Liner Repair |  | EA | 5 |  | 0 |  |  |  |  | 4"* |  | 30"x42" | 4' | *side-out let tee
59-65AA | 13 | Wetwell Liner, spray-on |  | SF | 84 |  | 0 |  |  |  |  | 4" |  | 30"x48" | 5'
| 14 | Intentionally Left Blank | [9 empty] | 4" |  | 36"x48" | 6'
71-72AA | 15 | Remove & Replace Ex. PVC Drain P-trap (regrout) |  | EA | 1 |  | 0 |  |  |  |  | 6" |  | 36"x60" | 6', 8'
| 16 | Intentionally Left Blank | [9 empty] | 8" |  | 36"x72" | 8'
73-77AA | 17 | Gate Valve, 2" |  | EA | 3 |  | 0
78-82AA | 18 | Check Valve, 2" |  | EA | 2 |  | 0
1-12P | 19 | Gate Valve, MJ, 2" |  | EA | 1 |  | 0
83-87AA | 20 | Intentionally Left Blank
106-110AA | 21 | Pipe, PVC (SCH 80), force main, 2" |  | LF | 10 |  | 0
88AA | 22 | Fittings, PVC | [9 empty] | Below | Above
| 22.1 | Intentionally Left Blank | [9 empty] | 0 | 2
| 22.2 | Cross, 2" |  | EA | 1 |  | 0 |  |  |  |  | 1 | 0
| 22.3 | 90, 2" |  | EA | 3 |  | 0 |  |  |  |  | 2 | 1
| 22.4 | Intentionally Left Blank | [9 empty] | 0 | 1
| 22.5 | 45, 2" |  | EA | 2 |  | 0
90-94AA | 23 | Intentionally Left Blank
95-96AA | 24 | Quick Coupler Adapter, aluminum, male, w/ alum dust cap, 2" |  | EA | 1 |  | 0
97AA | 25 | S.S. Adjustable Pipe Supports |  | EA | 3 |  | 0
| 26 | Intentionally Left Blank
| 27 | Concrete Slab, valve vault floor |  | EA | 1 |  | 0
116-123AA | 28 | Influent Line Plug, 8" |  | EA | 2 |  | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 1 |  | 0
129AA | 30 | Water Service Connection and Line, 2" |  | LF | 10 |  | 0
| 31 | Upgrade / Relocate Ex. Meter, Backflow, & Hose Bibb Assembly |  | EA | 1 |  | 0
| 32 | Replace Ex. Tapping Saddle; Install Brass Plug |  | EA | 1 |  | 0
1AB | 33 | Remove & Replace Electric Meter Can |  | EA | 1 |  | 0
2AB | 34 | Remove & Replace Fused Safety Switch (disconnect) |  | EA | 1 |  | 0
4AB | 35 | Remove & Replace Control Panel |  | EA | 1 |  | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 1 |  | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 1 |  | 0
| 37 | Junction Box, 304 SS |  | EA | 1 |  | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 30 |  | 0
25AB | 39 | Remove & Replace Electrical Service |  | LF | 10 |  | 0
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 1 |  | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 1 |  | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 1 |  | 0
| 43 | Washed Shell with Weed Barrier |  | SY | 66 |  | 0
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 42 |  | 0
19A | 45 | Intentionally Left Blank
| 46 | Sodding |  | SY | 100 |  | 0
53AA | 47 | Intentionally Left Blank
| 48 | Intentionally Left Blank
| 49 | Fill Dirt, clean and compacted |  | CY | 25 |  | 0
| 50 | Concrete Retaining Wall w/ Aluminum Safety Rail |  | LS | 1 |  | 0
| 51 | Intentionally Left Blank
| 52 | Intentionally Left Blank
| 53-62 | Intentionally Left Blank
|  | Subtotal Construction Cost |  |  |  |  | 0
| 63 | Mobilization |  | LS | 1 |  | 0
| 64 | Record Drawings* |  | LS | 1 |  | 0
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0
|  | Total Construction Cost with a project completion of 270 calendar days |  |  |  |  | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
taken from Lsinfo 2018
|  |  | Design Point: | 32 | @ | 132
No. of Pumps |  |  | Top Elevation: | 4.72 | NGVD | WW Depth:
2 |  |  | Bottom Elevation: | 0.09 | NGVD | 4.63
|  |  | Wet Well Dia: | 4 | ft
Add Stilling Well |  |  | WW2Cross: | 10 | ft
No |  |  | Cross2P.V.: | 4 | ft
|  |  | Top or Bottom Surface Area: | 13 | sq-ft
New Spray Liner |  |  | Total Internal Surface Area: | 84 | sq-ft
Yes |  |  | Wall Surface Area: | 58 | sq-ft
|  |  | Wet Well to be Raised/(Lowered): | 0 | ft
Above Ground Valve Assembly |  |  | Valve Vault to be Raised: | 0 | ft
No |  |  | Meter Vault to be Raised: | 0 | ft
Replace Guide Rails?
Yes |  |  |  | 1 pump | 2 pumps (150%) |  |  | DIA. | HDPE ID | PVC ID | Sch 80
|  | Dia. Disch. Pipe (in) | Design Flow (gpm) | Vel. In Disch. Pipe (f/s) | Vel. In Disch. Pipe (f/s) |  |  | 2 | 2.05 |  | 2.047
|  | #N/A | 32 | #N/A | #N/A |  |  | 4 | 3.89 | 4.27
Yes |  |  |  | #N/A |  |  |  | 6 | 5.59 | 6.13
No | [7 empty] | 8 | 7.34 | 8.04
|  |  |  | If Vel. In Disch. Pipe (1 pump) ≥ 8 f/s upsize pipe diameter |  |  |  | 10 | 8.96
[8 empty] | 12 | 10.66
Handrail, FDOT Index 850, LF

## Lakewood Meadows 388
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidders must provide prices for each available line item on each tab for their bid to be considered responsive.
LIFT STATION REHABILITATION - LAKEWOOD MEADOWS RTU 388 (Project No. 5156091)
| ITEM NO. | DESCRIPTION |  | U/M | QTY. | UNIT PRICE | EXTENDED PRICE ($)
1AA | 1 | Wetwell Cleaning |  | SF | 506 |  | 0
4-8AA | 2 | Wetwell Discharge Piping, HDPE DR-11, 6" |  | LF | 72 |  | 0 |  | 6
20-22AA | 3 | Pump Base Ells, BPIU-14 |  | EA | 2 |  | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 2 |  | 0
26-32AA | 5 | S.S. Pipe Bracing, 6 ft dia. |  | EA | 3 |  | 0
34-37AA | 6 | Intentionally Left Blank
| 6.1 | Intentionally Left Blank
| 7 | Replace Existing Top Slab
38-41AA | 7.1 | Wet Well, 12" thick |  | EA | 1 |  | 0
| 7.2 | Intentionally Left Blank
| 8 | PVC Vent, Sch 80, 6" |  | EA | 1 |  | 0
42-48AA | 9 | Aluminum Hatch Cover, 36" x 48", single door (Wetwell) |  | EA | 1 |  | 0 |  |  |  |  | Hatch Cover Size Requirements
42-48AA | 10 | Intentionally Left Blank | [9 empty] | Disch Pipe Size |  | Hatch Size | WW Dia. Range
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 48 |  | 0 |  |  |  |  | 3" |  | 30"x32" | 41" | *side-out let tee
54-58AA | 12 | Intentionally Left Blank | [9 empty] | 4"* |  | 30"x42" | 4' | *side-out let tee
59-65AA | 13 | Intentionally Left Blank | [9 empty] | 4" |  | 30"x48" | 5'
| 14 | Repair Ex. Liner, if required |  | SF | 250 |  | 0 |  |  |  |  | 4" |  | 36"x48" | 6'
71-72AA | 15 | Intentionally Left Blank | [9 empty] | 6" |  | 36"x60" | 6', 8'
| 16 | Grout Fill Ex. Drain, abandon |  | EA | 1 |  | 0 |  |  |  |  | 8" |  | 36"x72" | 8'
73-77AA | 17 | Gate Valve, FLG, 6" |  | EA | 3 |  | 0
78-82AA | 18 | Swing Check Valve, FLG, 6" |  | EA | 2 |  | 0
1-12P | 19 | Gate Valve, MJ, 6" |  | EA | 1 |  | 0
83-87AA | 20 | Pipe, D.I., FLG, 6" |  | LF | 5 |  | 0
106-110AA | 21 | Pipe, PVC (DR-18), 6" |  | LF | 10 |  | 0
88AA | 22 | Fittings, ductile iron | [9 empty] | Below | Above
| 22.1 | Tee, FLG, 6" |  | EA | 2 |  | 0 |  |  |  |  | 0 | 2
| 22.2 | Intentionally Left Blank | [9 empty] | 1 | 0
| 22.3 | 90, FLG, 6" |  | EA | 1 |  | 0 |  |  |  |  | 2 | 1
| 22.4 | 90, MJ, 6" |  | EA | 1 |  | 0 |  |  |  |  | 0 | 1
| 22.5 | Intentionally Left Blank
90-94AA | 23 | Coupling Adapters, D.I., FLG, 6" |  | EA | 1 |  | 0
95-96AA | 24 | Quick Coupler Adapter, aluminum, male, w/ alum dust cap, 6" |  | EA | 1 |  | 0
97AA | 25 | S.S. Adjustable Valve Supports, FLG attachment |  | EA | 3 |  | 0
| 26 | Abandon Existing Structure |  | EA | 1 |  | 0
| 27 | Concrete Slab, Valve Assembly |  | EA | 1 |  | 0
116-123AA | 28 | Influent Line Plug, 8" |  | EA | 1 |  | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 1 |  | 0
129AA | 30 | Water Service Connection and Line, 2" |  | LF | 10 |  | 0
| 31 | Upgrade / Relocate Ex. Meter, Backflow, & Hose Bibb Assembly |  | EA | 1 |  | 0
| 32 | Replace Ex. Tapping Saddle; Install Brass Plug |  | EA | 1 |  | 0
1AB | 33 | Remove & Replace Electric Meter Can |  | EA | 1 |  | 0
2AB | 34 | Remove & Replace Fused Safety Switch (disconnect) |  | EA | 1 |  | 0
4AB | 35 | Remove & Replace Control Panel |  | EA | 1 |  | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 1 |  | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 1 |  | 0
| 37 | Junction Box, 304 SS |  | EA | 1 |  | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 30 |  | 0
25AB | 39 | Remove & Replace Electrical Service |  | LF | 10 |  | 0
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 1 |  | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 1 |  | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 1 |  | 0
| 43 | Washed Shell with Weed Barrier |  | SY | 100 |  | 0
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 250 |  | 0
19A | 45 | Install New Lift Station Driveway, 6" thick concrete |  | SY | 45 |  | 0
| 46 | Sodding |  | SY | 20 |  | 0
53AA | 47 | Intentionally Left Blank
| 48 | Intentionally Left Blank
| 49 | Intentionally Left Blank
| 50 | Intentionally Left Blank
| 51 | Intentionally Left Blank
| 52 | Intentionally Left Blank
| 53-62 | Intentionally Left Blank
|  | Subtotal Construction Cost |  |  |  |  | 0
| 63 | Mobilization |  | LS | 1 |  | 0 | 10%
| 64 | Record Drawings |  | LS | 1 |  | 0 | 1%
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0
|  | Total Construction Cost with a project completion of 270 calendar days |  |  |  |  | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
taken from Lsinfo 2018
|  |  | Design Point: | 413 | @ | 32
No. of Pumps |  |  | Top Elevation: | 22 | NGVD | WW Depth:
2 |  |  | Bottom Elevation: | -1.84 | NGVD | 23.84
|  |  | Wet Well Dia: | 6 | ft
Add Stilling Well |  |  | WW2Cross: | 10 | ft
No |  |  | Cross2P.V.: | 5 | ft
|  |  | Top or Bottom Surface Area: | 29 | sq-ft
New Spray Liner |  |  | Total Internal Surface Area: | 506 | sq-ft
No |  |  | Wall Surface Area: | 448 | sq-ft
|  |  | Wet Well to be Raised/(Lowered): | 0 | ft
Above Ground Valve Assembly |  |  | Valve Vault to be Raised: | 0 | ft
Yes |  |  | Meter Vault to be Raised: | 0 | ft
Replace Guide Rails?
Yes |  |  |  | 1 pump | 2 pumps (150%) |  |  | DIA. | HDPE ID | PVC ID | Sch 80
|  | Dia. Disch. Pipe (in) | Design Flow (gpm) | Vel. In Disch. Pipe (f/s) | Vel. In Disch. Pipe (f/s) |  |  | 2 |  |  | 2.047
|  | 5.59 | 413 | 5.4018 | 8.1027 |  |  | 4 | 3.89 | 4.27
Yes |  |  |  | Keep Size |  |  |  | 6 | 5.59 | 6.13
No | [7 empty] | 8 | 7.34 | 8.04
|  |  |  | If Vel. In Disch. Pipe (1 pump) ≥ 8 f/s upsize pipe diameter |  |  |  | 10 | 8.96
[8 empty] | 12 | 10.66

## Mote Ranch 3 398
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidders must provide prices for each available line item on each tab for their bid to be considered responsive.
LIFT STATION REHABILITATION - MOTE RANCH 3 RTU 398 (Project No. 5156092)
| ITEM NO. | DESCRIPTION |  | U/M | QTY. | UNIT PRICE | EXTENDED PRICE ($)
1AA | 1 | Wetwell Cleaning |  | SF | 539 |  | 0
4-8AA | 2 | Wetwell Discharge Piping, HDPE DR-11, 4" |  | LF | 76 |  | 0 |  | 4
20-22AA | 3 | Pump Base Ells, BPIU-14 |  | EA | 2 |  | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 2 |  | 0
26-32AA | 5 | S.S. Pipe Bracing, 6 ft dia. |  | EA | 3 |  | 0
34-37AA | 6 | Intentionally Left Blank
| 6.1 | Intentionally Left Blank
| 7 | Replace Existing Top Slab
38-41AA | 7.1 | Wet Well, 12" thick |  | EA | 1 |  | 0
| 7.2 | Intentionally Left Blank
| 8 | PVC Vent, Sch 80, 4" |  | EA | 1 |  | 0
42-48AA | 9 | Aluminum Hatch Cover, 36" x 48", single door (Wetwell) |  | EA | 1 |  | 0 |  |  |  |  | Hatch Cover Size Requirements
42-48AA | 10 | Intentionally Left Blank | [9 empty] | Disch Pipe Size |  | Hatch Size | WW Dia. Range
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 52 |  | 0 |  |  |  |  | 3" |  | 30"x32" | 41" | *side-out let tee
54-58AA | 12 | Intentionally Left Blank | [9 empty] | 4"* |  | 30"x42" | 4' | *side-out let tee
59-65AA | 13 | Wetwell Liner, spray-on |  | SF | 539 |  | 0 |  |  |  |  | 4" |  | 30"x48" | 5'
| 14 | Remove Ex. Liner |  | SF | 539 |  | 0 |  |  |  |  | 4" |  | 36"x48" | 6'
71-72AA | 15 | Intentionally Left Blank | [9 empty] | 6" |  | 36"x60" | 6', 8'
| 16 | Grout Fill Ex. Drain, abandon |  | EA | 1 |  | 0 |  |  |  |  | 8" |  | 36"x72" | 8'
73-77AA | 17 | Gate Valve, FLG, 4" |  | EA | 3 |  | 0
78-82AA | 18 | Swing Check Valve, FLG, 4" |  | EA | 2 |  | 0
1-12P | 19 | Gate Valve, MJ, 4" |  | EA | 1 |  | 0
83-87AA | 20 | Pipe, D.I., FLG, 4" |  | LF | 5 |  | 0
106-110AA | 21 | Pipe, PVC (DR-18), 4" |  | LF | 25 |  | 0
88AA | 22 | Fittings, ductile iron | [9 empty] | Below | Above
| 22.1 | Tee, FLG, 4" |  | EA | 2 |  | 0 |  |  |  |  | 0 | 2
| 22.2 | Intentionally Left Blank | [9 empty] | 1 | 0
| 22.3 | 90, FLG, 4" |  | EA | 1 |  | 0 |  |  |  |  | 2 | 1
| 22.4 | 90, MJ, 4" |  | EA | 1 |  | 0 |  |  |  |  | 0 | 1
| 22.5 | 45, MJ, 4" |  | EA | 2 |  | 0
90-94AA | 23 | Coupling Adapters, D.I., FLG, 4" |  | EA | 1 |  | 0
95-96AA | 24 | Quick Coupler Adapter, aluminum, male, w/ alum dust cap, 4" |  | EA | 1 |  | 0
97AA | 25 | S.S. Adjustable Valve Supports, FLG attachment |  | EA | 2 |  | 0
| 26 | Abandon Existing Structure |  | EA | 1 |  | 0
| 27 | Concrete Slab, Valve Assembly |  | EA | 1 |  | 0
116-123AA | 28 | Influent Line Plug, 8" |  | EA | 1 |  | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 1 |  | 0
129AA | 30 | Water Service Connection and Line, 2" |  | LF | 10 |  | 0
| 31 | Intentionally Left Blank
| 32 | Replace Ex. Tapping Saddle; Install Brass Plug |  | EA | 1 |  | 0
1AB | 33 | Remove & Replace Electric Meter Can |  | EA | 1 |  | 0
2AB | 34 | Remove & Replace Fused Safety Switch (disconnect) |  | EA | 1 |  | 0
4AB | 35 | Remove & Replace Control Panel |  | EA | 1 |  | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 1 |  | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 1 |  | 0
| 37 | Junction Box, 304 SS |  | EA | 1 |  | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 30 |  | 0
25AB | 39 | Remove & Replace Electrical Service |  | LF | 10 |  | 0
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 1 |  | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 1 |  | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 1 |  | 0
| 43 | Intentionally Left Blank
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 270 |  | 0
19A | 45 | Install New Lift Station Driveway, 6" thick concrete |  | SY | 100 |  | 0
| 46 | Sodding |  | SY | 100 |  | 0
53AA | 47 | Intentionally Left Blank
| 48 | Tree/Brush Removal |  | EA | 4 |  | 0
| 49 | Intentionally Left Blank
| 50 | Intentionally Left Blank
| 51 | Intentionally Left Blank
| 52 | Intentionally Left Blank
| 53-62 | Intentionally Left Blank
|  | Subtotal Construction Cost |  |  |  |  | 0
| 63 | Mobilization |  | LS | 1 |  | 0 | 10%
| 64 | Record Drawings |  | LS | 1 |  | 0 | 1%
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0
|  | Total Construction Cost with a project completion of 270 calendar days |  |  |  |  | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
taken from Lsinfo 2018
|  |  | Design Point: | 128 | @ | 110
No. of Pumps |  |  | Top Elevation: | 20.5 | NGVD | WW Depth:
2 |  |  | Bottom Elevation: | -5.1 | NGVD | 25.6
|  |  | Wet Well Dia: | 6 | ft
Add Stilling Well |  |  | WW2Cross: | 10 | ft
No |  |  | Cross2P.V.: | 25 | ft
|  |  | Top or Bottom Surface Area: | 29 | sq-ft
New Spray Liner |  |  | Total Internal Surface Area: | 539 | sq-ft
Yes |  |  | Wall Surface Area: | 481 | sq-ft
|  |  | Wet Well to be Raised/(Lowered): | 0 | ft
Above Ground Valve Assembly |  |  | Valve Vault to be Raised: | 0 | ft
Yes |  |  | Meter Vault to be Raised: | 0 | ft
Replace Guide Rails?
Yes |  |  |  | 1 pump | 2 pumps (150%) |  |  | DIA. | HDPE ID | PVC ID | Sch 80
|  | Dia. Disch. Pipe (in) | Design Flow (gpm) | Vel. In Disch. Pipe (f/s) | Vel. In Disch. Pipe (f/s) |  |  | 2 |  |  | 2.047
|  | #N/A | 128 | #N/A | #N/A |  |  | 4 | 3.89 | 4.27
Yes |  |  |  | #N/A |  |  |  | 6 | 5.59 | 6.13
No | [7 empty] | 8 | 7.34 | 8.04
|  |  |  | If Vel. In Disch. Pipe (1 pump) ≥ 8 f/s upsize pipe diameter |  |  |  | 10 | 8.96
[8 empty] | 12 | 10.66

## 41A 454
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidders must provide prices for each available line item on each tab for their bid to be considered responsive.
LIFT STATION REHABILITATION - 41A RTU 454 (Project No. 5156093)
| ITEM NO. | DESCRIPTION |  | U/M | QTY. | UNIT PRICE | EXTENDED PRICE ($)
1AA | 1 | Wetwell Cleaning |  | SF | 1153 |  | 0
4-8AA | 2 | Intentionally Left Blank | [6 empty] | 10
20-22AA | 3 | Pump Base Ells, BPIU-16 |  | EA | 3 |  | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 3 |  | 0
26-32AA | 5 | S.S. Pipe Bracing, 10 ft dia. |  | EA | 3 |  | 0
34-37AA | 6 | Intentionally Left Blank
| 6.1 | Intentionally Left Blank
| 7 | Intentionally Left Blank
38-41AA | 7.1 | Intentionally Left Blank
| 7.2 | Intentionally Left Blank
| 8 | Intentionally Left Blank
42-48AA | 9 | Intentionally Left Blank | [9 empty] | Hatch Cover Size Requirements
42-48AA | 10 | Intentionally Left Blank | [9 empty] | Disch Pipe Size |  | Hatch Size | WW Dia. Range
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 63 |  | 0 |  |  |  |  | 3" |  | 30"x32" | 41" | *side-out let tee
54-58AA | 12 | Intentionally Left Blank | [9 empty] | 4"* |  | 30"x42" | 4' | *side-out let tee
59-65AA | 13 | Wetwell Liner, spray-on |  | SF | 1153 |  | 0 |  |  |  |  | 4" |  | 30"x48" | 5'
| 14 | Remove Ex. Liner |  | SF | 1153 |  | 0 |  |  |  |  | 4" |  | 36"x48" | 6'
71-72AA | 15 | Intentionally Left Blank | [9 empty] | 6" |  | 36"x60" | 6', 8'
| 16 | Intentionally Left Blank | [9 empty] | 8" |  | 36"x72" | 8'
73-77AA | 17 | Intentionally Left Blank
78-82AA | 18 | Intentionally Left Blank
1-12P | 19 | Intentionally Left Blank
83-87AA | 20 | Intentionally Left Blank
106-110AA | 21 | Intentionally Left Blank
88AA | 22 | Intentionally Left Blank | [9 empty] | Below | Above
| 22.1 | Intentionally Left Blank | [9 empty] | 0 | 2
| 22.2 | Intentionally Left Blank | [9 empty] | 1 | 0
| 22.3 | Intentionally Left Blank | [9 empty] | 2 | 1
| 22.4 | Intentionally Left Blank | [9 empty] | 0 | 1
| 22.5 | Intentionally Left Blank
90-94AA | 23 | Intentionally Left Blank
95-96AA | 24 | Intentionally Left Blank
97AA | 25 | Intentionally Left Blank
| 26 | Intentionally Left Blank
| 27 | Intentionally Left Blank
116-123AA | 28 | Influent Line Plug, 24" |  | EA | 1 |  | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 1 |  | 0
129AA | 30 | Intentionally Left Blank
| 31 | Intentionally Left Blank
| 32 | Intentionally Left Blank
1AB | 33 | Intentionally Left Blank
2AB | 34 | Intentionally Left Blank
4AB | 35 | Remove & Replace Control Panel |  | EA | 1 |  | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 1 |  | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 1 |  | 0
| 37 | Junction Box, 304 SS |  | EA | 1 |  | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 30 |  | 0
25AB | 39 | Intentionally Left Blank
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 1 |  | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 1 |  | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 1 |  | 0
| 43 | Intentionally Left Blank
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 761 |  | 0
19A | 45 | Intentionally Left Blank
| 46 | Intentionally Left Blank
53AA | 47 | New Conc. Floor & Fillet, 4,000 psi |  | CY | 10 |  | 0
| 48 | Intentionally Left Blank
| 49 | Intentionally Left Blank
| 50 | Intentionally Left Blank
| 51 | Restore Ex. Meter Vault |  | EA | 1 |  | 0
| 52 | Install Drop Bowl, gravity influent |  | EA | 1 |  | 0
| 53-62 | Intentionally Left Blank
|  | Subtotal Construction Cost |  |  |  |  | 0
| 63 | Mobilization |  | LS | 1 |  | 0 | 10%
| 64 | Record Drawings |  | LS | 1 |  | 0 | 1%
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0
|  | Total Construction Cost with a project completion of 270 calendar days |  |  |  |  | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
taken from Lsinfo 2018
|  |  | Design Point: | 2000 | @ | 50
No. of Pumps |  |  | Top Elevation: | 20.75 | NGVD | WW Depth:
3 |  |  | Bottom Elevation: | 0 | NGVD | 20.75
|  |  | Wet Well 10'x12' Rect.: | 12 | ft | 10 | ft
Add Stilling Well |  |  | WW2Cross: | 0 | ft
No |  |  | Cross2P.V.: | 0 | ft
|  |  | Top or Bottom Surface Area: | 120 | sq-ft
New Spray Liner |  |  | Total Internal Surface Area: | 1153 | sq-ft
Yes |  |  | Wall Surface Area: | 913 | sq-ft
|  |  | Wet Well to be Raised/(Lowered): | 0 | ft
Above Ground Valve Assembly |  |  | Valve Vault to be Raised: | 0 | ft
No |  |  | Meter Vault to be Raised: | 0 | ft
Replace Guide Rails?
Yes |  |  |  | 1 pump | 2 pumps (150%) |  |  | DIA. | HDPE ID | PVC ID | Sch 80
|  | Dia. Disch. Pipe (in) | Design Flow (gpm) | Vel. In Disch. Pipe (f/s) | Vel. In Disch. Pipe (f/s) |  |  | 2 |  |  | 2.047
|  | 8.96 | 2000 | 10.1818 | 15.2727 |  |  | 4 | 3.89 | 4.27
Yes |  |  |  | Upsize |  |  |  | 6 | 5.59 | 6.13
No | [7 empty] | 8 | 7.34 | 8.04
|  |  |  | If Vel. In Disch. Pipe (1 pump) ≥ 8 f/s upsize pipe diameter |  |  |  | 10 | 8.96
[8 empty] | 12 | 10.66

## Arnold Palmer Green 1 689
APPENDIX K, BID PRICING FORM
IFBC No 21-TA003622SAM
PROJECT NAME: SATELLITE LIFT STATION R&R 2020 GROUP 3
PROJECT NUMBER: 402-0019707
Bidders must provide prices for each available line item on each tab for their bid to be considered responsive.
LIFT STATION REHABILITATION - ARNOLD PALMER GREEN 1 RTU 689 (Project No. 5156094)
| ITEM NO. | DESCRIPTION |  | U/M | QTY. | UNIT PRICE | EXTENDED PRICE ($)
1AA | 1 | Wetwell Cleaning |  | SF | 776 |  | 0
4-8AA | 2 | Wetwell Discharge Piping, HDPE DR-11, 6" |  | LF | 78 |  | 0 |  | 6
20-22AA | 3 | Pump Base Ells, BPIU-14 |  | EA | 2 |  | 0
23-26AA | 4 | Pump Base Ell Mounting Plate |  | EA | 2 |  | 0
26-32AA | 5 | S.S. Pipe Bracing, 8 ft dia. |  | EA | 4 |  | 0
34-37AA | 6 | Modify Existing Rim Elevation
| 6.1 | Wet Well |  | VF | 2 |  | 0
| 7 | Replace Existing Top Slab
38-41AA | 7.1 | Wet Well |  | EA | 1 |  | 0
| 7.2 | Intentionally Left Blank
| 8 | PVC Vent, Sch 80, 6" |  | EA | 1 |  | 0
42-48AA | 9 | Aluminum Hatch Cover, 36" x 48", single door (Wetwell) |  | EA | 1 |  | 0 |  |  |  |  | Hatch Cover Size Requirements
42-48AA | 10 | Intentionally Left Blank | [9 empty] | Disch Pipe Size |  | Hatch Size | WW Dia. Range
49AA | 11 | 2" S.S.Pump Guide Rail System |  | LF | 54 |  | 0 |  |  |  |  | 3" |  | 30"x32" | 41" | *side-out let tee
54-58AA | 12 | Intentionally Left Blank | [9 empty] | 4"* |  | 30"x42" | 4' | *side-out let tee
59-65AA | 13 | Intentionally Left Blank | [9 empty] | 4" |  | 30"x48" | 5'
| 14 | Repair Ex. Liner, if required |  | SF | 250 |  | 0 |  |  |  |  | 4" |  | 36"x48" | 6'
71-72AA | 15 | Intentionally Left Blank | [9 empty] | 6" |  | 36"x60" | 6', 8'
| 16 | Grout Fill Ex. Drain, abandon |  | EA | 1 |  | 0 |  |  |  |  | 8" |  | 36"x72" | 8'
73-77AA | 17 | Gate Valve, FLG, 6" |  | EA | 3 |  | 0
78-82AA | 18 | Swing Check Valve, FLG, 6" |  | EA | 2 |  | 0
1-12P | 19 | Gate Valve, MJ, 6" |  | EA | 1 |  | 0
83-87AA | 20 | Pipe, D.I., FLG, 6" |  | LF | 5 |  | 0
106-110AA | 21 | Pipe, PVC (DR-18), 6" |  | LF | 10 |  | 0
88AA | 22 | Fittings, ductile iron | [9 empty] | Below | Above
| 22.1 | Tee, FLG, 6" |  | EA | 2 |  | 0 |  |  |  |  | 0 | 2
| 22.2 | Intentionally Left Blank | [9 empty] | 1 | 0
| 22.3 | 90, FLG, 6" |  | EA | 2 |  | 0 |  |  |  |  | 2 | 1
| 22.4 | 90, MJ, 6" |  | EA | 1 |  | 0 |  |  |  |  | 0 | 1
| 22.5 | 45, MJ, 6" |  | EA | 2 |  | 0
90-94AA | 23 | Coupling Adapters, D.I., FLG, 6" |  | EA | 1 |  | 0
95-96AA | 24 | Quick Coupler Adapter, aluminum, male, w/ alum dust cap, 6" |  | EA | 1 |  | 0
97AA | 25 | S.S. Adjustable Valve Supports, FLG attachment |  | EA | 2 |  | 0
| 26 | Abandon Existing Structure |  | EA | 1 |  | 0
| 27 | Concrete Slab, Valve Assembly |  | EA | 1 |  | 0
116-123AA | 28 | Influent Line Plug, 8" |  | EA | 1 |  | 0
124-127AA | 29 | By-Pass Pumping |  | LS | 1 |  | 0
129AA | 30 | Water Service Connection and Line, 2" |  | LF | 70 |  | 0
| 31 | Upgrade / Relocate Ex. Meter, Backflow, & Hose Bibb Assembly |  | EA | 1 |  | 0
| 32 | Replace Ex. Tapping Saddle; Install Brass Plug |  | EA | 1 |  | 0
1AB | 33 | Remove & Replace Electric Meter Can |  | EA | 1 |  | 0
2AB | 34 | Remove & Replace Fused Safety Switch (disconnect) |  | EA | 1 |  | 0
4AB | 35 | Remove & Replace Control Panel |  | EA | 1 |  | 0
| 35.1 | Includes TCU Bubbler Unit (TBU-360) by DFS |  | EA | 1 |  | 0
| 36 | TCU & Fiberglass Enclosure, DFS |  | EA | 1 |  | 0
| 37 | Junction Box, 304 SS |  | EA | 1 |  | 0
19AB | 38 | Remove & Replace Sch 80 PVC Conduit |  | LF | 30 |  | 0
25AB | 39 | Remove & Replace Electrical Service |  | LF | 10 |  | 0
29AB | 40 | Remove & Replace Electrical Mounting Structure |  | EA | 1 |  | 0
| 41 | Elect. System Study & Elect. Study Analysis, (NFPA 70E), complete |  | LS | 1 |  | 0
| 42 | Ex. Antenna Concrete Base, remove & disposal |  | LS | 1 |  | 0
| 43 | Washed Shell with Weed Barrier |  | SY | 40 |  | 0
17A | 44 | Concrete Repair, 2" thick, (inside wet well, if required) |  | SF | 388 |  | 0
19A | 45 | Install New Lift Station Driveway, 6" thick concrete |  | SY | 60 |  | 0
| 46 | Sodding |  | SY | 200 |  | 0
53AA | 47 | Intentionally Left Blank
| 48 | Intentionally Left Blank
| 49 | Fill Dirt, clean and compacted |  | CY | 10 |  | 0
| 50 | Intentionally Left Blank
| 51 | Intentionally Left Blank
| 52 | Intentionally Left Blank
|  | Subtotal Construction Cost |  |  |  |  | 0
EMERGENCY GENERATOR REMOVAL-EMERGENCY BACKUP PUMP INSTALLATION
| 53 | Site Demolition |  | LS | 1 |  | 0
| 54 | Reinforced Concrete Slab (poured in place) |  | SY | 15 |  | 0
| 55 | Emergency Backup Pump & Fuel Tank |  | LS | 1 |  | 0
| 56 | PVC Pipe (C900, DR-18), 6" (Pump Discharge Line) |  | LF | 26 |  | 0
| 57 | HDPE DR-11, 8" (Pump Suction Line) |  | LF | 32 |  | 0
| 58 | Ductile Iron Fittings
| 58.1 | Red., FLG, 4"x6" (pump connection fitting, adjust as necessary) |  | EA | 1 |  | 0
| 58.2 | Red., FLG, 4"x8" (pump connection fitting, adjust as necessary) |  | EA | 1 |  | 0
| 58.3 | 45, MJ, 6" |  | EA | 2 |  | 0
| 58.4 | 90, FLG, 6" |  | EA | 1 |  | 0
| 58.5 | 45, FLG, 8" |  | EA | 1 |  | 0
| 58.6 | 90, FLG. 8" |  | EA | 1 |  | 0
| 58.7 | 90, MJ, 8" |  | EA | 1 |  | 0
| 58.8 | 90, HDPE Molded , Fusion Welded, 8" |  | EA | 1 |  | 0
| 59 | Sch 80 PVC Conduit, 2" |  | LF | 15 |  | 0
36AB | 60 | Level Transducer, GXS3-PP300-A49-B49-50-C01-D49 |  | EA | 1 |  | 0
33AA | 61 | PVC Stilling Well, 6" |  | LF | 28 |  | 0
| 62 | Permits |  | LS | 1 |  | 0
|  | Generator Subtotal Construction Cost |  |  |  |  | 0
|  | Subtotal Construction & Generator Costs |  |  |  |  | 0
| 63 | Mobilization |  | LS | 1 |  | 0 | 10%
| 64 | Record Drawings |  | LS | 1 |  | 0 | 1%
| 65 | Contract Contingency (10% of Subtotal Construction Cost) |  |  | 10% |  | 0
|  | Total Construction Cost with a project completion of 270 calendar days |  |  |  |  | 0
*(% of Subtotal)
| Note: | Opinion of cost assumes construction to be completed by private contractor.
taken from Lsinfo 2018
|  |  | Design Point: | 477 | @ | 124
No. of Pumps |  |  | Top Elevation: | 44.3 | NGVD | WW Depth:
2 |  |  | Bottom Elevation: | 19.43 | NGVD | 26.87
|  |  | Wet Well Dia: | 8 | ft
Add Stilling Well |  |  | WW2Cross: | 10 | ft
No |  |  | Cross2P.V.: | 5 | ft
|  |  | Top or Bottom Surface Area: | 51 | sq-ft
New Spray Liner |  |  | Total Internal Surface Area: | 776 | sq-ft
No |  |  | Wall Surface Area: | 674 | sq-ft
|  |  | Wet Well to be Raised/(Lowered): | 2 | ft
Above Ground Valve Assembly |  |  | Valve Vault to be Raised: | 0 | ft
Yes |  |  | Meter Vault to be Raised: | 0 | ft
Replace Guide Rails?
Yes |  |  |  | 1 pump | 2 pumps (150%) |  |  | DIA. | HDPE ID | PVC ID | Sch 80
|  | Dia. Disch. Pipe (in) | Design Flow (gpm) | Vel. In Disch. Pipe (f/s) | Vel. In Disch. Pipe (f/s) |  |  | 2 |  |  | 2.047
|  | 5.59 | 477 | 6.2389 | 9.3583 |  |  | 4 | 3.89 | 4.27
Yes |  |  |  | Keep Size |  |  |  | 6 | 5.59 | 6.13
No | [7 empty] | 8 | 7.34 | 8.04
If Vel. In Disch. Pipe (1 pump) ≥ 8 f/s upsize pipe diameter